Power Systems Laboratory

User Manual

Department of Electrical and Computer Engineering

University of Minnesota

Revised : July 22, 2008

Textbook: First Course in Power Systems by Ned Mohan, www.mnpere.com.

Simulation Files: The simulation files mentioned in this lab manual are taken from the CD that accompanies the above Textbook.

Video Clips: The video clips mentioned in this lab manual are on the following website: www.ece.umn.edu/groups/power.  These are designed to show the usage of the following software programs: PSCAD-EMTDC, PowerWorld, and MATLAB/Simulink.

Laboratory Experiment 1

Visit to a Local Substation or a Generating Plant

Objective: To see firsthand apparatus that we will be studying in this course and learn about their role in operation and protection of power systems.

Laboratory Task: Visit a local substation.

Report:

Write a few sentences about each apparatus you saw, include its photograph if you were allowed to take it (of course with permission and always reference the source), and state its role, as you understand it at this stage in your study, in operation and protection of power systems.  State the approximate physical size and the electric ratings in terms of voltage, current, power, kVA etc.  These apparatus may include transmission line towers and their structure, transmission line conductors, their size and bundling, transformers, circuit breakers, surge arresters, relays, line traps for line-carrier communication, microwave towers, bus bars and their arrangement, substation grounding, battery backup as uninterruptible power supplies and so on.

Note:

It is not always possible to arrange such a visit due to a host of reasons.  In the following pages, photographs taken during a visit on May 16, 2006 to an HVDC substation are attached.  This visit was organized by Mr. Jack Christofersen, and hosted and conducted by Mr. David Eisenschenk of the Great River Energy Cooperative.  These photographs were taken by Prof. Bruce Wollenberg, who has kindly given his permission for them to be included here.

(a)

(b)

(c)

(d)

(e)

(f)

(g)

(h)

(i)

(j)

Laboratory Experiment 2

Familiarization with PSCAD/EMTDC and

Understanding of Reactive Power and Power Factor Correction in AC Circuits

Objectives:

- Learn the usage of PSCAD/EMTDC in modeling of ac circuits and plotting of results.

- Understanding reactive power and power factor in single-phase and three-phase circuits.

Install PSCAD-EMTDC and PowerWorld: see video clip# 1.

Laboratory Tasks and Report:

- Familiarization with PSCAD/EMTDC:

Read ahead the “Simple Guide to using PSCAD/EMTDC” below to model ac circuits for this experiment and plot their results.

- Single-Phase AC Circuit in Steady State: (RLC.psc; see video clip# 2)

- Model a single-phase ac circuit where a voltage source  at the fundamental frequency of 60 Hz is supplying an inductive series R-L load, with an impedance of .  .  Plot the waveforms for the voltage , the current , the instantaneous power  and the average power  delivered to the load; all in the same plot.

- Calculate a capacitive reactance , to be connected in parallel with the load, to bring the overall power factor seen from the source to unity.  Plot  and , the instantaneous power  and the average power  delivered to the load; all in the same plot.

- Three-Phase AC Circuit in Steady State:

- Connect a three-phase circuit in a balanced-wye where the per-phase circuit is the same as the single-phase circuit above.  Calculate , , , , , and the sum of the three instantaneous power .

- Connect the capacitive reactance  calculated in step 2b, in parallel with the load in each phase, to bring the per-phase power factor to unity.  Plot  and , the instantaneous power  and the average power  delivered to the load; all in the same plot.

Simple Guide to using PSCAD/EMTDC

- Launch PSCAD (student version) from Start Menu.

- Creating new project:

Click on File/New/Case – A new project entitled ‘noname’ appears in the left workspace window, indicating that a new project is created.

- Setting active project:

In the workspace window, right click on the title of an inactive project and select Set as active.

- Saving active project:

Click on File/Save Active Project. Select appropriate folder and save the project as ‘Lab1’ or any other name.

- Adding components to a project:

Double click on master library in left top workspace. Navigate to the area containing desired component. Right click on component and select Copy. Open the project where you wish to add the component (double click on ‘project name’), right click over blank area and select Paste. (Note: There are many other ways to add a component to a project)

- Setting Properties:

To set the properties double click on any component and change the parameters.

At the top of the parameter dialog is a drop list, which contains list of all parameter dialog pages. If only one page exists, then the drop list will be disabled. For e.g. if you double click on resistor, it will ask for only resistance value.

- Making connections between components:

Click Wire Mode button in the main toolbar. Move the mouse pointer onto the project page. The mouse pointer will have turned into a pencil, which indicates you are in Wire mode. To draw a wire, move the cursor to the node where you want line to start and left click. Move the cursor to where you want the line to end and right-click to complete the wire. Multi-segment Wires may be built by continuing to left click at different points. To turn off Wire Mode, press Esc key.

- Measurement:

To measure currents and voltages ammeter and voltmeter are provided on toolbar on right. Ammeter should be connected in series.

To plot currents and voltages use output channel and data signal label on toolbar, as shown in the fig below

where VHigh, is data signal label and is same signal name given in voltmeter or ammeter. Voltmeter /Ammeter signal name and data label signal name should match. In the output channel parameter dialog give title, unit, scale factor and min/max limits.

- Adding a Graph Frame:

Right click on the Output Channel component. Select Input/Output Reference/Add Overlay Graph with Signal. This will create a new graph frame, overlay graph and a curve simultaneously. For adding more graphs on same graph frame, right click on graph frame and click Add Overlay Graph (Analog). This will add another graph on same frame. To put a curve on this graph Ctrl+click on output channel and drag it on the graph. Curve corresponding to that output channel will be added on to graph. When you run the simulation curves will be automatically plotted on this graph.

Press Y and X buttons to see complete curve (zoom out).

- Setting time step and simulation time:

Right click on blank space in project, select Project Settings. In runtime tab you can set simulation time, time step and plot step.

- To simulate the project:

Click on Build/R.

Laboratory Experiment 3

Obtaining Parameters of a 345 kV Transmission Line and Modeling it in PSCAD/EMTDC

Objectives:  Obtaining the parameters of a 345 kV transmission line and modeling it in PSCAD/EMTDC.

Laboratory Tasks and Report:

Tasks

- Consider a 345-kV transmission line consists of three-conductor-flat towers shown in Fig. 4-8.  This transmission system consists of a single-conductor per phase, which is a Bluebird ACSR conductor with a diameter of 1.762 inches.  The PSCAD/EMTDC file for this 345-kV single-conductor line is LineParameters.psc (see video clip# 3), which is located in this folder.  Double click on it to open it and execute it to calculate line constants.  Compare the results with those given in Example 4-2.

Fig. 4-8 A 345-kV, single-conductor per phase, transmission system.

- The PSCAD/EMTDC file for a 345-kV double-conductor line is LineParameters_Bundled.psc, which is located in this folder.  Double click on it to open it and execute it to calculate line constants.  Compare the results with those in Task 1.

- A 200 km long 345-kV line has the parameters given in the Table below.  Neglect the resistance.  Measure the reactive power at both ends under the following two levels of loading if both ends are held at the voltages of 1 per unit: (a) 1.5 times SIL, and (b) 0.75 times SIL.  The PSCAD/EMTDC file for modeling this transmission line is TransmissionLine.psc (see video clip# 4), which is located in this folder.  Double click on it to open it and execute it.

Table 4-1

Transmission Line Parameters with Bundled Conductors at 60 Hz

| Nominal Voltage |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| 345 kV | 0.037 | 0.376 | 4.518 | 280 (use 288.48) | 425 MW (use 412.16) |

Help with Transmission Line Constants in PSCAD/EMTDC:

Task 1:

- Take T-Line i.e. transmission line from toolbar.

- Double click on T-Line, in the configuration parameters dialog select Termination style as Direct connection

- Set other parameters as per requirement

- Click on edit to edit tower and conductor data

- Select and delete ‘frequency dependent model’ block. Right click on blank area and select Bergeron model

- Again right click on blank area to select type of tower. There are 12 tower types to choose from

- Double click on Tower structure to edit the data as below

| Component | Properties |
| --- | --- |
| Line constants 3 conductor flat tower | Tower Data: Here you can edit Height of conductors, Horizontal Spacing between conductors etc. Also you can specify no. of ground wires and transposed lines or untransposed lines. Conductor Data: In this either you can select conductor from a library or can specify conductor radius and DC resistance. Change the library path to this C:\Program Files\PSCAD420Eval\examples\Relay_Cases\conductor.clb Ground Wire Data: As in conductor data you can specify ground wire data using library or inputting radius and resistance of ground wire. Also you can specify sag for ground wires, height of ground wires and spacing between ground wires. Conductor bundling X, Y data: If bundled conductors are used, then their X, Y positions can be specified here. |

- Right click on blank space and click on additional options. After pasting it, double click on additional options and change the output file display settings in the dialog box appropriately.

- To solve the line constants, right click on blank space and select ‘solve constants’.

- Click on ‘output’ at the bottom to see the results.

Laboratory Experiment 4

Power Flow using MATLAB and PowerWorld

Objective:  To carry out power flow calculations using MATLAB and PowerWorld program.

Laboratory Tasks and Report:

- The MATLAB files to calculate power flow in the example 3-bus power system using both Newton-Raphson and Gauss-Seidel methods are included in this folder  (see video clip#  6).

  - Execute the Newton_Raphson_task_1a.m file and obtain power and reactive power flow through all the transmission lines (both ends) and provided by the generators at buses 1 and 2 using both the methods. Draw a diagram of the three bus system and add the values of the P and Q flows and the P and Q bus injections to the diagram.

  - Execute the Gauss_seidel_task_1a program. Does it get to the same solution? Why does it take so many more iterations?

  - The line shunt capacitances have been added as described in Chapter 5,  execute the Newton_Raphson_task_1b.m file to obtain power and reactive power flow and compare the results with part (a). Explain all differences.

- The PowerWorld file to calculate power flow in the example 3-bus power system is Three_Bus_PowerFlow.pwb (see video clip#  5), which is included in this folder.

  - Execute this file and obtain the results to confirm those from the MATLAB programs in step 1.

  - Comment on the nature of buses 1 and 2.

  - Add the line shunt capacitances as in part 1(c) and compare results.

  - Limit the reactive power from generator 2 to be in a range  and see the influence on the bus 2 voltage and power flows on the lines.

  - Raise the power delivered to bus 3 by clicking on the up arrow next to the real power displayed. How much can you deliver until voltage drops to 0.95 pu? How much can you deliver until it drops to 0.90 pu?

Newton Raphson Power Flow Program

% Example 5-4 Power Flow in a 3-bus Test System

clear

j = sqrt(-1);

V = zeros(3,1);

S = zeros(3,1);

Mismatch = zeros(3,1);

% ---------- Input line impedances ------------- %

Z = [0 0.0047 + 0.0474i 0.0062 + 0.0632i

0.0047 + 0.0474i 0 0.0047 + 0.0474i

0.0062 + 0.0632i 0.0047 + 0.0474i 0];

%---------Base Values ---------%

kVLL=345;

MVA3Ph=100;

Zbase=kVLL^2/MVA3Ph;

XL_km=0.376;                        % ohm/km at 60 Hz

RL_km= 0.037; B_km=4.5;             % B in micro-mho/km

%---------Line Susceptances--------%

B13_Micro_Mho=4.5*200;               %200 km long

B12_Micro_Mho=4.5*150;               %150 km long

B23_Micro_Mho=4.5*150;               %150 km long

%---------Line impedances------------%

Z13_ohm=(RL_km+j*XL_km)*200;         %200 km long

Z12_ohm=(RL_km+j*XL_km)*150;         %150 km long

Z23_ohm=(RL_km+j*XL_km)*150;         %150 km long

%------- line impedances in per unit--------%

Z13=Z13_ohm/Zbase;

Z12=Z12_ohm/Zbase;

Z23=Z23_ohm/Zbase;

%-------- susceptances in per unit----------%

B13=B13_Micro_Mho*Zbase*10^-6;

B12=B12_Micro_Mho*Zbase*10^-6;

B23=B23_Micro_Mho*Zbase*10^-6;

%---------- YBUS Creation-------------%

Y(1,1)=1/Z12 + 1/Z13;

Y(1,2)=-1/Z12;

Y(1,3)=-1/Z13;

Y(2,1)=-1/Z12;

Y(2,2)=1/Z12 + 1/Z23;

Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13;

Y(3,2)=-1/Z23;

Y(3,3)=1/Z13 + 1/Z23;

Y               % Print Y=G+jB Admittance Matrix

%----------Conductance Values------------%

G(1,1)=real(Y(1,1));

G(1,2)=real(Y(1,2));

G(1,3)=real(Y(1,3));

G(2,1)=real(Y(2,1));

G(2,2)=real(Y(2,2));

G(2,3)=real(Y(2,3));

G(3,1)=real(Y(3,1));

G(3,2)=real(Y(3,2));

G(3,3)=real(Y(3,3));

%--------Susceptance Values----------%

B(1,1)=imag(Y(1,1));

B(1,2)=imag(Y(1,2));

B(1,3)=imag(Y(1,3));

B(2,1)=imag(Y(2,1));

B(2,2)=imag(Y(2,2));

B(2,3)=imag(Y(2,3));

B(3,1)=imag(Y(3,1));

B(3,2)=imag(Y(3,2));

B(3,3)=imag(Y(3,3));

%--------- Given Specifications in pu----------%

V1MAG=1.0;

ANG1=0;

V2MAG=1.05;

P2sp=2.0;

P3sp=-5.0;

Q3sp=-1.0;

% -------------Calulate ANG2, V3MAG and ANG3---------------%

% ----Solution Parameters----%

Tolerance= 0.001;

Iter_Max=10;

%----- Initialization-------%

Iter=0;

i=0;

ConvFlag=1;

ANG2=0;

ANG3=0;

V3MAG=1.0;

delANG2=0;

delANG3=0;

delMAG3=0;

%------------------ Start Iteration Process for N-R-----------------%

while( ConvFlag==1 & Iter < Iter_Max)

Iter=Iter+1;

i=i+1;

ANG2=ANG2+delANG2;

ANG3=ANG3+delANG3;

V3MAG=V3MAG+delMAG3;

%------- Creation of Jacobian J--------%

% J(1,1)=dP2/dAng2; Eq. 9-26; k=2, m=1,3

J(1,1)=V2MAG*(V1MAG*(-G(2,1)*sin(ANG2-ANG1)+B(2,1)*cos(ANG2-ANG1)) + V3MAG*(-G(2,3)*sin(ANG2-ANG3)+B(2,3)*cos(ANG2-ANG3)));

% J(1,2)=dP2/dAng3; Eq. 9-27; k=2, j=3

J(1,2)=V2MAG*(V3MAG*(G(2,3)*sin(ANG2-ANG3)-B(2,3)*cos(ANG2-ANG3)));

% J(1,3)=dP2/dMAG3; Eq. 9-29; k=2, j=3

J(1,3)=V2MAG*((G(2,3)*cos(ANG2-ANG3)+B(2,3)*sin(ANG2-ANG3)));

% J(2,1)=dP3/dAng2; Eq. 9-27; k=3, j=2

J(2,1)=V3MAG*(V2MAG*(G(3,2)*sin(ANG3-ANG2)-B(3,2)*cos(ANG3-ANG2)));

% J(2,2)=dP3/dAng3; Eq. 9-26; k=3, m=1,2

J(2,2)=V3MAG*(V1MAG*(-G(3,1)*sin(ANG3-ANG1)+B(3,1)*cos(ANG3-ANG1)) + V2MAG*(-G(3,2)*sin(ANG3-ANG2)+B(3,2)*cos(ANG3-ANG2)));

% J(2,3)=dP3/dMAG3; Eq. 9-28; k=3, m=1,2

J(2,3)=2*G(3,3)*V3MAG + V1MAG*(G(3,1)*cos(ANG3-ANG1)+B(3,1)*sin(ANG3-ANG1)) + V2MAG*(G(3,2)*cos(ANG3-ANG2)+B(3,2)*sin(ANG3-ANG2));

% J(3,1)=dQ3/dAng2; Eq. 9-31; k=3, j=2

J(3,1)=V3MAG*(V2MAG*(G(3,2)*cos(ANG3-ANG2)-B(3,2)*sin(ANG3-ANG2)));

% J(3,2)=dQ3/dAng3; Eq. 9-30; k=3, m=1,2

J(3,2)=V3MAG*(V1MAG*(G(3,1)*cos(ANG3-ANG1)+B(3,1)*sin(ANG3-ANG1)) + V2MAG*(G(3,2)*cos(ANG3-ANG2)+B(3,2)*sin(ANG3-ANG2)));

% J(3,3)=dQ3/dMAG3; Eq. 9-32; k=3, m=1,2

J(3,3)=- 2*B(3,3)*V3MAG + V1MAG*(G(3,1)*sin(ANG3-ANG1)-B(3,1)*cos(ANG3-ANG1))  + V2MAG*(G(3,2)*sin(ANG3-ANG2)-B(3,2)*cos(ANG3-ANG2));

% ---------Bus Voltages--------%

V(1)=V1MAG*exp(j*ANG1);

V(2)=V2MAG*exp(j*ANG2);

V(3)=V3MAG*exp(j*ANG3);

% -------Injected currents into Buses-------%

Iinj=Y*V;

%------- P and Q Injected into Buses--------%

S(1)=V(1)*conj(Iinj(1));

S(2)=V(2)*conj(Iinj(2));

S(3)=V(3)*conj(Iinj(3));

% -----Mismatch at PQ and PV buses-------%

Mismatch(1)=P2sp-real(S(2));

Mismatch(2)=P3sp-real(S(3));

Mismatch(3)=Q3sp-imag(S(3));

% -------calculate new delta values for ANG2, ANG3, and MAG3------&

del=inv(J)*Mismatch;

delANG2=del(1);

delANG3=del(2);

delMAG3=del(3);

% -------Calculate Power Flow on the Transmission Lines-------%

P12=real(V(1)*conj((V(1)-V(2))/Z12));    Q12=imag(V(1)*conj((V(1)-V(2))/Z12)); % at Bus 1

P13=real(V(1)*conj((V(1)-V(3))/Z13));    Q13=imag(V(1)*conj((V(1)-V(3))/Z13)); % at Bus 1

P21=real(V(2)*conj((V(2)-V(1))/Z12));    Q21=imag(V(2)*conj((V(2)-V(1))/Z12)); % at Bus 2

P23=real(V(2)*conj((V(2)-V(3))/Z23));    Q23=imag(V(2)*conj((V(2)-V(3))/Z23)); % at Bus 2

P31=real(V(3)*conj((V(3)-V(1))/Z13));    Q31=imag(V(3)*conj((V(3)-V(1))/Z13)); % at Bus 3

P32=real(V(3)*conj((V(3)-V(2))/Z23));    Q32=imag(V(3)*conj((V(3)-V(2))/Z23)); % at Bus 3

P1=real(S(1));

Q1=imag(S(1));

P2=real(S(2));

Q2=imag(S(2));

P3=real(S(3));

Q3=imag(S(3));

%--------Display voltage and P,Q values at each iteration-------%

fprintf('\n %s %2d %s \n', 'Iter ',Iter, '  Mismatch 1   Mismatch 2   Mismatch 3 ')

fprintf('             %7.4f        %7.4f      %7.4f \n', Mismatch(1), Mismatch(2), Mismatch(3) );

if max(abs(Mismatch)) > Tolerance,

ConvFlag=1;

else

ConvFlag=0;

end

end

J,                                            %  Print Final Jacobian Matrix

ANG2DEG=ANG2*180/pi,

ANG3DEG=ANG3*180/pi,

V3MAG,

%-------Display Power Flows on the buses---------%

fprintf('\n %s','Flows on Line 1-2')

fprintf('\n  %s \n', ' P12       Q12        P21        Q21 ')

fprintf('   %7.4f   %7.4f   %7.4f   %7.4f  \n',  P12, Q12 ,P21, Q21)

fprintf('\n %s','Flows on Line 1-3')

fprintf('\n  %s \n', ' P13       Q13        P31        Q31 ')

fprintf(' %7.4f   %7.4f   %7.4f   %7.4f  \n', P13, Q13 ,P31, Q31)

fprintf('\n %s','Flows on Line 2-3')

fprintf('\n  %s \n',  ' P23       Q23        P32        Q32 ')

fprintf('  %7.4f   %7.4f   %7.4f   %7.4f  \n',  P23, Q23 ,P32, Q32)

fprintf('\n %s','Net P,Q at Buses')

fprintf('\n %s \n', '  P1          Q1          P2          Q2         P3         Q3  ')

fprintf('  %7.4f    %7.4f    %7.4f    %7.4f     %7.4f     %7.4f    \n',  P1, Q1, P2, Q2, P3, Q3)

Gauss-Seidel Power Flow Program

Iter = 0;

Maxiter = 20;

converge = 0;

tolerance  = 0.001;

j = sqrt(-1);

% ---------- Input line impedances ------------- %

Z = [0 0.0047 + 0.0474i 0.0062 + 0.0632i

0.0047 + 0.0474i 0 0.0047 + 0.0474i

0.0062 + 0.0632i 0.0047 + 0.0474i 0];

% ---------- Base Values ----------- %

kVLL=345;

MVA3Ph=100;

Zbase=kVLL^2/MVA3Ph;

XL_km=0.376;                             % ohm/km at 60 Hz

RL_km= 0.037; B_km=4.5;                  % B in micro-mho/km

Z13_ohm=(RL_km+j*XL_km)*200;             %200 km long

B13_Micro_Mho=4.5*200;                   %200 km long

Z12_ohm=(RL_km+j*XL_km)*150;             %150 km long

B12_Micro_Mho=4.5*150;                   %150 km long

Z23_ohm=(RL_km+j*XL_km)*150;             %150 km long

B23_Micro_Mho=4.5*150;                   %150 km long

%--------- line impedances in per unit ----------%

Z13=Z13_ohm/Zbase;

Z12=Z12_ohm/Zbase;

Z23=Z23_ohm/Zbase;

%--------- susceptances in per unit ----------%

B13=B13_Micro_Mho*Zbase*10^-6;

B12=B12_Micro_Mho*Zbase*10^-6;

B23=B23_Micro_Mho*Zbase*10^-6;

%-------Finding the admittance matrix---------%

Y(1,1)=1/Z12 + 1/Z13;

Y(1,2)=-1/Z12;

Y(1,3)=-1/Z13;

Y(2,1)=-1/Z12;

Y(2,2)=1/Z12 + 1/Z23;

Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13;

Y(3,2)=-1/Z23;

Y(3,3)=1/Z13 + 1/Z23;

G = real(Y);

B = imag(Y);

% ------- Initialize line variables --------- %

I = zeros(1,length(Z));

P = zeros(1,length(Z));

Q = zeros(1,length(Z));

S = zeros(1,length(Z));

% -------- Input bus parameters --------- %

v = ones(1,length(Z));

%angle = zeros(length(Z),1);

Pload = zeros(1,length(Z));

Qload = zeros(1,length(Z));

Psched = zeros(1,length(Z));

Qsched = zeros(1,length(Z));

Bustype(1) = 'S';                          % PQ bus

Bustype(2) = 'G';                          % PV bus

Bustype(3) = 'L';                          % PQ bus

v(2) = 1.05;

Pload(2) = -2;

Pload(3) = 5;

Qload(3) = 1;

% ------ Set up power schedule --------- %

totload = 0.0;

for i = 1:length(Z)

Psched(i)= -Pload(i);

Qsched(i)= -Qload(i);

totload = totload + Pload(i);

end

% --- Calculate P and Q at each bus ----- %

for i = 1:length(Z)

I(i) = 0.0 + sqrt(-1)*0.0;

for j = 1:length(Z)

I(i) = I(i) + Y(i,j)*v(j);

end

S(i) = v(i) * conj(I(i));

P(i) = real(S(i));

Q(i) = imag(S(i));

end

% ------- Display bus voltages ---------- %

fprintf('\n %s %2d %s \n', 'Iter ',Iter, '  Vreal   Vimag   Vmag   Vangle     P      Q ')

for i = 1:length(Z)

vitermag = abs(v(i));

viterang = (180./pi)*atan2(imag(v(i)),real(v(i)));

fprintf(' %s %2d %7.4f %7.4f %7.4f %7.4f %7.4f %7.4f \n',' Bus ',i, real(v(i)), imag(v(i)), vitermag, viterang, P(i), Q(i) )

end

while converge == 0

Iter = Iter + 1;

MAXDP = 0.0;

MAXDPbus = 0;

MAXDQ = 0.0;

MAXDQbus = 0;

for i = 1 : length(Z)

%---------calculate net P and Q at bus i--------%

I(i) = 0.0 + sqrt(-1)*0.0;

for j = 1:length(Z)

I(i) = I(i) + Y(i,j)*v(j);

end

S(i) = v(i) * conj(I(i));

P(i) = real(S(i));

Q(i) = imag(S(i));

if Bustype(i) == 'G'

Qsched(i) = Q(i);

end

deltap(i) = abs(P(i) - Psched(i));

deltaq(i) = 0.0;

if Bustype(i) == 'L'

deltaq(i) = abs(Q(i) - Qsched(i));

end

if Bustype(i) == 'S'

deltap(i) = 0.0;

deltaq(i) = 0.0;

end

if Bustype(i) ~= 'S'

if deltap(i) > MAXDP

MAXDP = deltap(i);

MAXDPbus = i;

end

if deltaq(i) > MAXDQ

MAXDQ = deltaq(i);

MAXDQbus = i;

end

%--------- Y * V for row i of Y matrix without Yii term---------%

sum = 0.0;

for j = 1:length(Z)

if j ~= i

sum = sum + Y(i,j)*v(j);

end

end

vnew = (1.0/Y(i,i))*( ((Psched(i) - sqrt(-1)*Qsched(i))/(conj(v(i)))) - sum);

v(i) = vnew;

end

end

%------------ Print and save result from last iteration-----------%

%-----calculate net P and Q at bus i-----%

for i = 1:length(Z)

I(i) = 0.0 + sqrt(-1)*0.0;

for j = 1:length(Z)

I(i) = I(i) + Y(i,j)*v(j);

end

S(i) = v(i) * conj(I(i));

P(i) = real(S(i));

Q(i) = imag(S(i));

if Bustype(i) == 'G'

Qsched(i) = Q(i);

end

end

fprintf('\n %s %2d %s \n', 'Iter ',Iter, '  Vreal   Vimag   Vmag   Vangle     P      Q ')

for i = 1:length(Z)

vitermag = abs(v(i));

viterang = (180./pi)*atan2(imag(v(i)),real(v(i)));

fprintf(' %s %2d %7.4f %7.4f %7.4f %7.4f %7.4f %7.4f \n',' Bus ',i, real(v(i)), imag(v(i)), vitermag, viterang, P(i), Q(i) )

end

% -------- check for convergence ---------- %

if MAXDP < tolerance

if MAXDQ < tolerance

converge = 1;

end

end

if Iter > Maxiter

converge = 1;

end

end

3Bus_PowerFlow.pwb

slack

Problem 5-8

Confirm the MATLAB Results of

Example 5-4.

3

500

MW

100

Mvar

1

2

69 MW

-111 Mvar

29 Mvar

7 Mvar

236 MW

239 MW

264 MW

-107 Mvar

268 MW

148 Mvar

0.98 pu

-8.79 Deg

1.00 pu

0.00 Deg

1.05 pu

-2.07 Deg

200 MW

267 Mvar

308 MW

-81 Mvar

68 MW

119 Mvar

Laboratory Experiment 5

Including Transformers in Power Flow using PowerWorld and Confirmation by MATLAB

Objectives:  To look at the influence of including a tap-changer and a phase-shifter on power flow and bus voltages.

Laboratory Tasks and Report:

- Including a Tap Changer (PowerFlow_AutoTransformer.pwb; see video clip# 7)

  - An Autotransformer is added between buses 1 and 4 (newly created) as shown in the PowerWorld file PowerFlow_AutoTransformer.pwb, which is located in this Folder.  Double click on this file or open it through PowerWorld.  The tap-ratio between buses 1 and 4 is such that .  Compare this case with that in Example 5-4 for the various bus voltages and the power flow on various lines due to this tap ratio.

  - Represent this auto-transformer by means of a pi-circuit of Fig. 6-17b in a MATLAB program, using the results of part a, to confirm the results of part a.

- Including a Phase-Shifter (PowerFlow_PhaseShift.pwb; see video clip# 7)

  - A phase-shift transformer is added between buses 1 and 4 (newly created) as shown in the PowerWorld file PowerFlow_PhaseShift.pwb, which is located in this Folder.  Double click on this file or open it through PowerWorld.  The phase-shift between buses 1 and 4 is such that  results in .  Compare this case with that in Example 5-4 for the various bus voltages and the power flow on various lines due to this phase shift.

  - Represent this phase-shift transformer by means of Eq. 6-32 in a MATLAB program, using the results of part a, to confirm the results of part a.

PowerFlow_AutoTransformer.pwb

slack

Problem 6-18

Add an tap-changing auto-transformer

as shown.

3

500 MW

100 Mvar

1

2

90 MW

-112 Mvar

70 Mvar

-40 Mvar

215 MW

218 MW

285 MW

-60 Mvar

289 MW

101 Mvar

1.00 pu

-9.86 Deg

1.00 pu

0.00 Deg

1.05 pu

-2.62 Deg

200 MW

223 Mvar

308 MW

-32 Mvar

4

1.06

tap

1.05 pu

-2.54 Deg

89 MW

122 Mvar

PowerFlow_PhaseShift.pwb

slack

Problem 6-19

Add a phase-shifting auto-transformer

as shown.

3

500 MW

100 Mvar

1

2

226 MW

-115 Mvar

27 Mvar

-22 Mvar

86 MW

86 MW

414 MW

-78 Mvar

423 MW

167 Mvar

0.97 pu

-17.02 Deg

1.00 pu

0.00 Deg

1.05 pu

-6.15 Deg

200 MW

313 Mvar

312 MW

-86 Mvar

4

0.99 pu

-13.89 Deg

-12.89

deg

223 MW

146 Mvar

Laboratory Experiment 6

Including an HVDC Transmission Line for Power Flow Calculations in PowerWorld and Modeling of Thyristor Converters in PSCAD/EMTDC

Objectives:

- To include an HVDC transmission line and see its effect on power transfer on other transmission line.

- To understand the operating principle of 12-pulse thyristor converters used in HVDC transmission systems.

Laboratory Tasks and Report:

- The transmission line between buses 1 and 3 is an HVDC line, as described in the PowerWorld file PowerFlow_HVDCline.pwb (see video clip# 8), which is located in this Folder.  Double click on this file or open it through PowerWorld.  Look at various characteristics of this HVDC system by examining its parameters; see dialog boxes below.  Compare this case with that in Example 5-4 for the various bus voltages and the power flow on various lines due to this HVDC line.

- Obtain the waveforms of individual Rectifier DC voltage and combined 12-pulse DC voltage output , for different firing angles , in a 12-pulse thyristor converter operating in a rectifier-mode described by the PSCAD/EMTDC file in this folder called HVDC_Rectifier.psc (see video clip# 9).  Source: Courtesy of Prof. Ani Golé of the University of Manitoba.

- Obtain the waveforms of individual inverter DC voltage and combined 12-pulse DC voltage input ,for different firing angles in a 12-pulse thyristor converter operating in the inverter-mode described by the PSCAD/EMTDC file in this folder called HVDC_Inverter.psc (see video clip# 9).  Source: Courtesy of Prof. Ani Golé of the University of Manitoba.

- By using the formula (7-12) and (7-13), for different firing angles, calculate the DC voltage and match with the value obtained from the waveform.                      For Rectifier: w*Ls = 13.6791 ohm, VLL=213 kV, Id= Obtain from simulation For Inverter: w*Ls=13.1843 ohm, VLL=207 kV, Id= Obtain from simulation.

- Obtain the waveforms of the input and output currents for both the transformers in rectifier and inverter. Observe the phase shift between the primary and secondary of Wye-Delta transformer.

- Obtain harmonic components of secondary line current of Wye-Delta Transformer and harmonic components of the source current in the rectifier and inverter. What is the significant difference between two of them? Why?

PowerFlow_HVDCline.pwb

slack

Problem 7-22

HVDC Line between Buses 1 and

3 is set to deliver 200 MW to

Bus3.The voltage at the inverter

terminal is 250 kV.

HVDC LINE

1

315 MW

-48 Mvar

2

200 MW

423 Mvar

3

500

MW

100

Mvar

161 MW

-115 Mvar

350 MW

-198 Mvar

359 MW

289 Mvar

1.00 pu

0.00 Deg

0.92 pu

-13.84 Deg

1.05 pu

-4.46 Deg

154 MW

150 MW

159 MW

133 Mvar

HVDC_Rectifier.psc

HVDC_Inverter.psc

Laboratory Experiment 7

Power Quality

Objectives:  To obtain the current harmonics drawn by power electronics interface.

Laboratory Tasks and Report:

- Calculate the displacement power factor, power factor and the total harmonic distortion associated with the power-electronics interface described in the PSCAD/EMTDC file PowerQuality.psc. See video clip# 10.

Help with PowerQuality.psc

Build the circuit as shown below

FFT and harmonic distortion blocks are taken from CSMF library.

Voltage and currents are plotted as described in first few experiments.

Laboratory Experiment 8

Synchronous Generators

Objectives:  To obtain the effect of sudden short-circuit on a synchronous generator output.

Laboratory Tasks and Report:

- Model a short-circuit on a synchronous generator as described by the PSCAD/EMTDC file SynchGen.psc.  Obtain various waveforms and comment on them. See video clip# 11.

- Plot Ef/Xd” , Ef/Xd’, Ef/Xd and Phase A line current together, to verify the peak current transition at the three transient modes.

SynchGen.psc

Laboratory Experiment 9

Voltage Regulation

Objectives:

- To study the effect of real and reactive powers on bus voltages.

- Modeling of Thyristor Controlled Reactors (TCR).

- Modeling of Thyristor Controlled Series Capacitors (TCSC).

Laboratory Tasks and Report:

- In the PowerWorld example VoltageRegulation.pwb, vary the reactive power consumed at Bus 3 in a range from 300 MAVR to -300 MVAR and plot its effect on voltage magnitudes at Buses 3 and 2.

- Model a TCR as described by the PSCAD/EMTDC file TCR.psc (see video clip# 12).  Obtain various waveforms and comment on them.

- Model a TCSC as described by the PSCAD/EMTDC file TCSC.psc (see video clip# 13).  Obtain various waveforms and comment on them.

VoltageRegulation.pwb

slack

Problem 5-8

Confirm the MATLAB Results of

Example 5-4.

3

500 MW

100

Mvar

1

2

69 MW

-111 Mvar

29 Mvar

7 Mvar

236 MW

239 MW

264 MW

-107 Mvar

268 MW

148 Mvar

0.98 pu

-8.79 Deg

1.00 pu

0.00 Deg

1.05 pu

-2.07 Deg

200 MW

267 Mvar

308 MW

-81 Mvar

68 MW

119 Mvar

TCR.psc

TCSC.psc

Laboratory Experiment 10

Transient Stability using MATLAB

Objectives:  To calculate transient stability in a 3-bus example power system.

Laboratory Tasks and Report:

The MATLAB file to calculate Transient Stability in the example 3-bus power system is TransientStability.m, which is included in this folder.  See video clip# 14.

  - Annotate this file based on the material and equations of Chapter 11.

  - Execute this file get the plots of rotor angles of generators 1 and 2.

  - Double the fault time and observe the effect on stability.

  - Assume that a three-phase fault occurs on line between buses 2 and 3, one-third away from bus 2.  The duration and the clearing time are the same as in the original case.  Modify the program and calculate the transient stability.

TransientStability.m

% Example 11-3 Swing Curves

clear all

j = sqrt(-1);

XL_km=0.367, % ohm/km at 60 Hz

RL_km= 0.1*XL_km; % Resistance in ohm/km

KV_LL= 345; MVA_Base=100; % common 3-phase base

Z_Base=KV_LL^2/MVA_Base; % common base

% YBUS Creation

Z13_ohm=(RL_km+j*XL_km)*200, B13_Micro_Mho=4.5*200, % Line 1-3 is 200 km long

Z12_ohm=(RL_km+j*XL_km)*150, B12_Micro_Mho=4.5*150, % Line 1-2 is 150 km long

Z23_ohm=(RL_km+j*XL_km)*150, B23_Micro_Mho=4.5*150, % Line 2-3 is 150 km long

Z13=Z13_ohm/Z_Base, Z12=Z12_ohm/Z_Base, Z23=Z23_ohm/Z_Base, % line impedances in per unit

Y(1,1)=1/Z12 + 1/Z13; Y(1,2)=-1/Z12; Y(1,3)=-1/Z13;

Y(2,1)=-1/Z12; Y(2,2)=1/Z12 + 1/Z23; Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13; Y(3,2)=-1/Z23; Y(3,3)=1/Z13 + 1/Z23;

G(1,1)=real(Y(1,1)); B(1,1)=imag(Y(1,1)); G(1,2)=real(Y(1,2)); B(1,2)=imag(Y(1,2)); G(1,3)=real(Y(1,3)); B(1,3)=imag(Y(1,3));

G(2,1)=real(Y(2,1)); B(2,1)=imag(Y(2,1)); G(2,2)=real(Y(2,2)); B(2,2)=imag(Y(2,2)); G(2,3)=real(Y(2,3)); B(2,3)=imag(Y(2,3));

G(3,1)=real(Y(3,1)); B(3,1)=imag(Y(3,1)); G(3,2)=real(Y(3,2)); B(3,2)=imag(Y(3,2)); G(3,3)=real(Y(3,3)); B(3,3)=imag(Y(3,3));

% Given Specifications

V1MAG=1.0; ANG1=0; V2MAG=1.03; P2sp=5.0; P3sp=-9.0; Q3sp=-4.0;

% Solution Parameters

Tolerance= 0.001; Iter_Max=10;

% Initialization

Iter=0; ConvFlag=1;

ANG2=0; ANG3=0; V3MAG=1.0;

delANG2=0; delANG3=0; delMAG3=0;

% Start Iteration Process for N-R

while( ConvFlag==1 & Iter < Iter_Max)

Iter=Iter+1,

ANG2=ANG2+delANG2;

ANG3=ANG3+delANG3;

V3MAG=V3MAG+delMAG3;

% Creation of Jacobian J

% J(1,1)=dP2/dAng2; k=2, m=1,3

J(1,1)=V2MAG*(V1MAG*(-G(2,1)*sin(ANG2-ANG1)+B(2,1)*cos(ANG2-ANG1)) + V3MAG*(-G(2,3)*sin(ANG2-ANG3)+B(2,3)*cos(ANG2-ANG3)));

% J(1,2)=dP2/dAng3; k=2, j=3

J(1,2)=V2MAG*(V3MAG*(G(2,3)*sin(ANG2-ANG3)-B(2,3)*cos(ANG2-ANG3)));

% J(1,3)=dP2/dMAG3; k=2, j=3

J(1,3)=V2MAG*((G(2,3)*cos(ANG2-ANG3)+B(2,3)*sin(ANG2-ANG3)));

% J(2,1)=dP3/dAng2; k=3, j=2

J(2,1)=V3MAG*(V2MAG*(G(3,2)*sin(ANG3-ANG2)-B(3,2)*cos(ANG3-ANG2)));

% J(2,2)=dP3/dAng3; k=3, m=1,2

J(2,2)=V3MAG*(V1MAG*(-G(3,1)*sin(ANG3-ANG1)+B(3,1)*cos(ANG3-ANG1)) + V2MAG*(-G(3,2)*sin(ANG3-ANG2)+B(3,2)*cos(ANG3-ANG2)));

% J(2,3)=dP3/dMAG3; k=3, m=1,2

J(2,3)=2*G(3,3)*V3MAG + V1MAG*(G(3,1)*cos(ANG3-ANG1)+B(3,1)*sin(ANG3-ANG1)) + V2MAG*(G(3,2)*cos(ANG3-ANG2)+B(3,2)*sin(ANG3-ANG2));

% J(3,1)=dQ3/dAng2; k=3, j=2

J(3,1)=V3MAG*(V2MAG*(G(3,2)*cos(ANG3-ANG2)-B(3,2)*sin(ANG3-ANG2)));

% J(3,2)=dQ3/dAng3; k=3, m=1,2

J(3,2)=V3MAG*(V1MAG*(G(3,1)*cos(ANG3-ANG1)+B(3,1)*sin(ANG3-ANG1)) + V2MAG*(G(3,2)*cos(ANG3-ANG2)+B(3,2)*sin(ANG3-ANG2)));

% J(3,3)=dQ3/dMAG3; k=3, m=1,2

J(3,3)=- 2*B(3,3)*V3MAG + V1MAG*(G(3,1)*sin(ANG3-ANG1)-B(3,1)*cos(ANG3-ANG1))  + V2MAG*(G(3,2)*sin(ANG3-ANG2)-B(3,2)*cos(ANG3-ANG2));

% Voltages

V(1,1)=V1MAG*exp(j*ANG1);

V(2,1)=V2MAG*exp(j*ANG2);

V(3,1)=V3MAG*exp(j*ANG3);

% Injected currents

Iinj=Y*V

% P and Q Injected

S(1,1)=V(1,1)*conj(Iinj(1)); S(2,1)=V(2,1)*conj(Iinj(2)); S(3,1)=V(3,1)*conj(Iinj(3));

% Mismatch at PQ and PV buses

Mismatch(1,1)=P2sp-real(S(2,1)); Mismatch(2,1)=P3sp-real(S(3,1)); Mismatch(3,1)=Q3sp-imag(S(3,1));

% calculate new delta values for ANG2, ANG3, and MAG3

del=inv(J)*Mismatch;

delANG2=del(1); delANG3=del(2); delMAG3=del(3);

if max(abs(Mismatch)) > Tolerance,

ConvFlag=1

else

ConvFlag=0;

end

end

Pm1=real(S(1,1))

Pm2=real(S(2,1))

P3=-real(S(3,1))

Q3=-imag(S(3,1))

ZLoad=V(3,1)/(-Iinj(3,1))

Xtr1_PU=0.12*MVA_Base/500;                    % Transformer base is 500 MVA

S_Gen1=500;

XdP1_PU=0.23*(22/KV_LL)^2*(MVA_Base/S_Gen1); % Gen XdP is 0.23pu on the base of 500MVA and 22kVLL

S_Gen2=600;

Xtr2_PU=0.12*MVA_Base/600;                   % Transformer base is 600 MVA

XdP2_PU=0.23*(22/KV_LL)^2*(MVA_Base/S_Gen2); % Gen XdP is 0.23pu on the base of 600MVA and 22kVLL

H_Gen=3.5; wsyn=377;

H1=H_Gen*(S_Gen1/MVA_Base);

H2=H_Gen*(S_Gen2/MVA_Base);

X1=XdP1_PU+Xtr1_PU; X2=XdP2_PU+Xtr2_PU;

% Pre-Fault (Pre) steady state

EP1=V(1,1)+j*X1*Iinj(1,1);

EP2=V(2,1)+j*X2*Iinj(2,1);

EP1MAG=abs(EP1); EP2MAG=abs(EP2);

DT=0.0001;

% Pre-Fault Transient

Pe1=Pm1; Pe2=Pm2;

Del1(1)=angle(EP1), Del2(1)=angle(EP2), w1(1)=wsyn; w2(1)=wsyn; time1(1)=0; DelREF=0;

DelDIFF1_DEG(1)=(Del1(1)-DelREF)*180/pi;

DelDIFF2_DEG(1)=(Del2(1)-DelREF)*180/pi;

imax=1000

for i=2:imax

time1(i)=time1(i-1)+DT;

w1(i)=w1(i-1)+(wsyn/(2*H1))*(Pm1-Pe1)*DT;

w2(i)=w2(i-1)+(wsyn/(2*H2))*(Pm2-Pe2)*DT;

Del1(i)=Del1(i-1)+w1(i-1)*DT;

Del2(i)=Del2(i-1)+w2(i-1)*DT;

EP1=EP1MAG*(cos(Del1(i))+j*sin(Del1(i)));

EP2=EP2MAG*(cos(Del2(i))+j*sin(Del2(i)));

I_Norton(1,1)=EP1/(j*X1); I_Norton(2,1)=EP2/(j*X2); I_Norton(3,1)=0;

Y(1,1)=1/(j*X1)+1/Z12 + 1/Z13; Y(1,2)=-1/Z12; Y(1,3)=-1/Z13;

Y(2,1)=-1/Z12; Y(2,2)=1/(j*X2)+1/Z12 + 1/Z23; Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13; Y(3,2)=-1/Z23; Y(3,3)=1/ZLoad+1/Z13 + 1/Z23;

V=inv(Y)*I_Norton;

Pe1=real(V(1,1)*conj(I_Norton(1,1)));

Pe2=real(V(2,1)*conj(I_Norton(2,1)));

DelREF=DelREF+DT*wsyn;

DelDIFF1_DEG(i)=(Del1(i)-DelREF)*180/pi;

DelDIFF2_DEG(i)=(Del2(i)-DelREF)*180/pi;

DelDIFF(i)=DelDIFF1_DEG(i)-DelDIFF2_DEG(i);

end

% During Fault Transient

kmax=5000

for k=1:kmax

i=imax+k;

time1(i)=time1(i-1)+DT;

w1(i)=w1(i-1)+(wsyn/(2*H1))*(Pm1-Pe1)*DT;

w2(i)=w2(i-1)+(wsyn/(2*H2))*(Pm2-Pe2)*DT;

Del1(i)=Del1(i-1)+w1(i-1)*DT;

Del2(i)=Del2(i-1)+w2(i-1)*DT;

EP1=EP1MAG*(cos(Del1(i))+j*sin(Del1(i)));

EP2=EP2MAG*(cos(Del2(i))+j*sin(Del2(i)));

I_Norton(1,1)=EP1/(j*X1); I_Norton(2,1)=EP2/(j*X2); I_Norton(3,1)=0;

Y(1,1)=1/(j*X1)+1/(Z12/3) + 1/Z13; Y(1,2)=0; Y(1,3)=-1/Z13;

Y(2,1)=0; Y(2,2)=1/(j*X2)+1/(2*Z12/3)+ 1/Z23; Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13; Y(3,2)=-1/Z23; Y(3,3)=1/ZLoad+1/Z13 + 1/Z23;

V=inv(Y)*I_Norton;

Pe1=real(V(1,1)*conj(I_Norton(1,1)));

Pe2=real(V(2,1)*conj(I_Norton(2,1)));

DelREF=DelREF+DT*wsyn;

DelDIFF1_DEG(i)=(Del1(i)-DelREF)*180/pi;

DelDIFF2_DEG(i)=(Del2(i)-DelREF)*180/pi;

DelDIFF(i)=DelDIFF1_DEG(i)-DelDIFF2_DEG(i);

end

% Post Fault Transient

nmax=10000

for n=1:nmax

i=imax+kmax+n;

time1(i)=time1(i-1)+DT;

w1(i)=w1(i-1)+(wsyn/(2*H1))*(Pm1-Pe1)*DT;

w2(i)=w2(i-1)+(wsyn/(2*H2))*(Pm2-Pe2)*DT;

Del1(i)=Del1(i-1)+w1(i-1)*DT;

Del2(i)=Del2(i-1)+w2(i-1)*DT;

EP1=EP1MAG*(cos(Del1(i))+j*sin(Del1(i)));

EP2=EP2MAG*(cos(Del2(i))+j*sin(Del2(i)));

I_Norton(1,1)=EP1/(j*X1); I_Norton(2,1)=EP2/(j*X2); I_Norton(3,1)=0;

Y(1,1)=1/(j*X1)+ 1/Z13; Y(1,2)=0; Y(1,3)=-1/Z13;

Y(2,1)=0; Y(2,2)=1/(j*X2)+ 1/Z23; Y(2,3)=-1/Z23;

Y(3,1)=-1/Z13; Y(3,2)=-1/Z23; Y(3,3)=1/ZLoad+1/Z13 + 1/Z23;

V=inv(Y)*I_Norton;

Pe1=real(V(1,1)*conj(I_Norton(1,1)));

Pe2=real(V(2,1)*conj(I_Norton(2,1)));

DelREF=DelREF+DT*wsyn;

DelDIFF1_DEG(i)=(Del1(i)-DelREF)*180/pi;

DelDIFF2_DEG(i)=(Del2(i)-DelREF)*180/pi;

DelDIFF(i)=DelDIFF1_DEG(i)-DelDIFF2_DEG(i);

end

% plot(time1,w1,time1,w2)

plot(time1,DelDIFF1_DEG,time1,DelDIFF2_DEG)

%plot(time1,DelDIFF)

Laboratory Experiment 11

AGC using Simulink and Economic Dispatch using PowerWorld

Objectives:  Study the dynamic interaction between two control areas using Simulink modeling and economic dispatch using PowerWorld.

Laboratory Tasks and Report:

- Study the dynamic interaction between two control areas using Simulink modeling.  The MATLAB file for this is AGC_Data.m, which is located in this Folder.  First launch MATLAB and open this file through it, and then execute it.  Then double click on the Simulink file AGC.mdl located in this folder.  Look at the various waveforms and comment on them.  Adapted from Reference 6 in Chapter 12. See video clip# 15.

- In PowerWorld, assume that the generation at Bus 2 is by two generators with different marginal costs, as shown in Load_Sharing.pwb.  Justify the load sharing between the generators.

AGC_Data.m

% Data for Example 12-3

H=5.3; % H=5.3 seconds

M1=(2*H)/(2*pi*60) % 2*pi*60 denotes the synchronous speed in rad/s

D1=0.75/(2*pi*60) % D1 is the damping coefficient

T12=0.1;

R1=0.167;

Tg1=.26;

Ts1=.26;

DL1=1; % 1 percent so the results are in per cent

DL2=0;

B1=1/R1+D1;

thetar=0;

K1=0.001*((2*pi*60)); % Controller gain for the ACE loop

AGC.mdl

Load_Sharing.pwb

slack

Problem 5-8

Confirm the MATLAB Results of

Example 5-4.

3

500 MW

100 Mvar

1

2

73 MW

-97 Mvar

27 Mvar

-6 Mvar

179 MW

321 MW

-94 Mvar

326 MW

149 Mvar

0.98 pu

-6.63 Deg

1.00 pu

0.00 Deg

1.05 pu

1.64 Deg

100 MW

127 Mvar

108 MW

-70 Mvar

300 MW

127 Mvar

74 MW

104 Mvar

181 MW

Laboratory Experiment 12

Transmission Line Short Circuit Faults using MATLAB and PowerWorld, and Overloading of Transmission Lines using PowerWorld

Objectives:  To study the effect of short-circuit faults and overloading of transmission lines.

Laboratory Tasks and Report:

- Simulate the fault in Example 13-2.  The MATLAB file for this example is SimpleSystemFault.m, which is located in this Folder.  First launch MATLAB and open this file through it, and then execute it.  The PowerWorld file for this example is SimpleSystemFault.pwb; double click on it and compare results with that from the MATLAB simulation.

- The PowerWorld file for this example is ShortCircuitFault.pwb (see video clips# 16 and 17), which is located in this Folder; double click on it and comment on results.

SimpleSystemFault.m

% Example 13-2; simple system

% Fault; 3-phase at bus 2

%Pre-Fault

V3_a1=0.98*exp(-j*11.79*pi/180);

I3_a1=(1/0.98)*exp(-j*11.79*pi/180);

Rload=0.98*0.98,

Ea=1+j*0.12*I3_a1,

[Th_Ea,Amp_Ea]=cart2pol(real(Ea),imag(Ea));

Th_Ea_deg=Th_Ea*180/pi,

Amp_Ea

Power=Ea*conj(I3_a1),

% 3-phase fault at bus 2

Ifault=Ea/(j*(0.12+0.1)),

[ang,Ifault_Mag]=cart2pol(real(Ifault),imag(Ifault));

Ifault_AngDEG=ang*180/pi,

Ifault_Mag

% SLG fault at bus 2

ITH=Ea/(j*0.32+Rload);

VTH=(j*0.1+Rload)*ITH;

ZTH=(j*0.1+Rload)*(j*0.22)/((j*0.1+Rload)+(j*0.22));

Z2=(j*0.1+Rload)*(j*0.22)/((j*0.1+Rload)+(j*0.22));

Z0=(j*0.2+Rload)*(j*0.10)/((j*0.2+Rload)+(j*0.10)); % delta wye-grounded transfomer bypasses X0 of generator

Ia1=VTH/(ZTH+Z2+Z0);

Ifault=3*Ia1;

[ang,Ifault_Mag]=cart2pol(real(Ifault),imag(Ifault));

Ifault_AngDEG=ang*180/pi,

Ifault_Mag

SimpleSystemFault.pwb

slack

Example 13-2

Simple system Fault

1

100 MW

21 Mvar

3

100 MW

0 Mvar

2

10 Mvar

0 Mvar

100 MW

100 MW

1.00 pu

0.00 Deg

0.98 pu

-11.79 Deg

0.98 pu

-5.83 Deg

ShortCircuitFault.pwb

slack

Example 13-3

4

308 MW

80 Mvar

5

200 MW

171 Mvar

3

500 MW

100 Mvar

1

2

69 Mvar

-27 Mvar

239 MW

243 MW

261 MW

-73 Mvar

265 MW

114 Mvar

200 MW

-146 Mvar

308 MW

-39 Mvar

1.00 pu

0.00 Deg

0.93 pu

-16.74 Deg

0.98 pu

-7.26 Deg

0.99 pu

-9.19 Deg

1.05 pu

-4.77 Deg

66 MW

-30 Mvar

65 MW

32 Mvar

Laboratory Experiment 13

Switching Over-Voltages and Modeling of Surge Arresters using PSCAD/EMTDC

Objectives:  To study over-voltages resulting from switching of transmission lines and limiting them by sing ZnO arresters.

Laboratory Tasks and Report:

- Model the reclosing of a transmission line as described by the PSCAD/EMTDC file TL_Energization.psc (see video clip# 18).  Obtain various waveforms and comment on them.

- Include the pre-insertion resistors, as described by the PSCAD/EMTDC file TL_Energization_Preinsertion.psc (see video clip# 18).  Obtain various waveforms and comment on them.

- Model the surge arresters to limit the over-voltages at the receiving end to 400 kV.  Obtain various waveforms and comment on them; TL_Energization_MOV.psc (see video clip# 18).

TL_Energization.psc

TL_Energization_Preinsertion.psc

TL_Energization_MOV.psc